## Slide 1: Bayesian Uncertainty Quantification of Physical Models in Thermal-Hydraulics System Codes
Damar Wicaksono (Thesis Directors: Prof. A. Pautz & Mr. O. Zerkak)
PhD Defense, EPF Lausanne, 19.01.2018

## Slide 2: Safety Analysis of LWR under LBLOCA: Show max. clad temperature < safety limit
Cold Leg
Hot Leg
Gas Phase
Liquid Phase
Double-ended
Guillotine Break
Emergency Injection
Two-phase
hydraulics
Heat conduction through solids
Reactor Core
Reactor Pressure Vessel
Clad Temperature
Time
Safety Limit
Notes: To put things into context let’s revisit the role of simulation in the safety analysis of NPP, in this case under LBLOCA in perhaps rather simplistic view.
We make prediction whether some safety criteria is within the safety limit.
Simulation by system code is based on the simulation of the two phase flow in the coolant circuit.

## Slide 3: Forward Uncertainty Quantification: Uncertain Inputs Uncertain Outputs
Forward Model (Code)
Uncertain Inputs
(random variables)
Uncertain Outputs
Statistical Analysis of ``Quantities of Interest’’
Decision Making
Material properties
Initial conditions
Boundary conditions
Physical model parameters
Clad Temperature
Safety Limit
Safe/Fail, Accept/Reject, etc.
Monte Carlo simulation (multiple code runs)
e.g., PCT
Notes: Give the general impression first from left to right
And the main ingredient of this analysis is the uncertain inputs

## Slide 4: Physical Model Parameters: post-Critical Heat Flux (CHF) Flow Regimes
pre-CHF
(Steam Convection)
Dispersed Flow Film Boiling (DFFB)
Interpolatory (Inverted Slug)
Inverted Annular Film Boiling (IAFB)
Transition Boiling
pre-CHF
(Nucleate Boiling)
Mass
Momentum
Energy
Closure Laws
Parametric
models
Notes: What are these physical model parameters?
Simulation of two phase flows are based on solving a set of balance equation.
Closure laws describe the interaction between phases in each distinct **pre-determined** flow regime
Take for example the phenomenological models that describe two phase flow during a reflood of a dry channel
Here is system code TRACE
Try to squeeze in a wall temperature profile along the axial of the rod.

## Slide 5: Origin of Uncertainty in Physical Model Parameters
FLECHT-SEASET
Westinghouse, USA
Excerpt from the TRACE Code Theory Manual:
“…the approximate value of the coefficient in Eq. (4-119) was determined from data comparisons with FLECHT-SEASET high flooding rate reflood data…” (pp. 164)
“In TRACE, the above interfacial drag coefficient has been reduced by a factor of ¾ to better match FLECHT-SEASET high flooding rate reflood data, so…” (pp. 166)
No statement of uncertainty on these parameters
Notes: Where is this uncertainty coming from
Note that the parameters become somehow an adjustment factor
The uncertainty of the calibration or fitting was not reported and such adjustment might not conform with probabilistic framework we use in propagation anyway
We need more systematic effort to define uncertainty

## Slide 6: Research Objectives
Given experimental data from a Separate Effect Test Facility (SETF), develop a methodology to:
quantify the uncertainty of physical model parameters in a TH System Code
to be propagated within statistical uncertainty analysis framework.
Calibration
Pre-calibration uncertainties
Post-calibration uncertainties
Experimental Data from SETF

## Slide 7: Scope of Research (1/2): Statistical Framework
Methods are non-intrusive
Methods require less assumptions about the underlying model
Results conform with probabilistic framework for UQ
Methods tend to be expensive
(require numerous code runs)
1. Global Sensitivity Analysis
2. Metamodeling
3. Bayesian Calibration
4. Uncertainty Propagation
Prior uncertainties
Posterior uncertainties
Reduced parameter sets
Notes: To answer those questions, we adapt and implement statistical methodologies derived from applied statistics especially related to the design and analysis of computer experiments.
And we don’t develop codes, it is worthwhile to develop methods that is applied outside the code implementation.
Don’t list the tools, state that it will serve as an outline of the presentation.
They are steps not tools

## Slide 8: Scope of Research (2/2): FEBA Separate Effect Test Facility (SETF)
FEBA Reflood Tests were conducted at Kfz Karlsruhe (KIT) during 1980s for investigating bottom reflood using rod simulators (NiCr)
Three types of measurements were taken:
Clad temperature (8 axial locations)
Pressure drop (4 axial segments)
Liquid carryover
Main analyses are based on Test No. 216:

## Slide 9: Scope of Research (2/2): TRACE Model of FEBA SETF
Powered Heater Rods
Housing/Enclosure
Spacer grid
Inlet flow
Upper plenum
Backpressure
  (4) Experimental boundary conditions (, , etc.)
  (9) Material properties (etc.)
  (2) Spacer grid model ()
  (10) Post-CHF closure relations (IAFB wall , DFFB interfacial drag, etc.)
  (1) Quench temperature
  (1) Transition boiling
Model
parameters
Controllable inputs
27 Parameters are required to specify the model:
With flat independent uncertainties, either in linear or log scales
Notes: The method is adapted and demonstrated directly to solve this problem.
The problem is used in the OECD/NEA PREMIUM Benchmark

## Slide 10: Statistical Framework (1/4): Global Sensitivity Analysis
1. Global Sensitivity Analysis
Gaussian Process Metamodeling
Bayesian Calibration
Uncertainty Propagation
How to approximate the input/output of the forward model?
How to make the inference (quantification)?
Is the quantified uncertainty useful?
27 initial parameters
(minutes/run)
(MBytes/run)
How to select the important parameters?
Clad Temperature [K]
Pressure Drop [bar]
Time [s]
Liquid Carryover [kg]
Propagation based on 1’000 samples
Identify the least influential parameters, and exclude them
Nominal parameter
Notes: Uncertainty propagation using prior pdfs and 1’000 samples. Bands are constructed based on the 95% probability (2.5th – 97.5th percentile).

## Slide 13: Global Sensitivity Analysis for Screening: The Morris Screening and Sobol’ Total-Effect
Sensitivity Measure
Number of Replications / Samples
replications code runs
samples code runs
Elementary effect
Perturbation of one parameter at a time
Grid size
Sobol’ total-effect index for :
Results on TC4 output
Notes: Formula
Meaning
Computation notes
Why we consider the two

## Slide 14: Uncertainty Propagation using Influential vs. Non-Influential Parameters
Clad Temperature [K]
Pressure Drop [bar]
Time [s]
Liquid Carryover [kg]
12 Influential
15 Non-influential
Parameter subsets
Uncertainty propagation using 2 parameter subsets and 500 Monte Carlo samples
12 parameters are influential:
(4) (8)
Boundary conditions
Closure laws and spacer grid
Notes: State that FDA is also in the thesis

## Slide 15: Statistical Framework (2/4): Metamodeling
1. Global Sensitivity Analysis
2. Metamodeling
How to select the important parameters?
How to approximate the input/output of a computer model?
27 initial parameters
12 influential parameters
Construct a metamodel for fast and efficient approximation
Metamodel: “a model of a model” or a surrogate

## Slide 16: Gaussian Process (GP) Metamodel
Prior
Data
Posterior
Probability distribution of functions
mean function
process variance
correlation (kernel) function
Gaussian Process
Gaussian process is a Gaussian with continuous variates:
Application in Regression
Notes: Main message is GP can be used to represent wide array of function using minimal number of parameters (or hyper parameters)

## Slide 17: Constructing GP Metamodel: Training and Testing
Testing
Design of Experiment
Training Runs
Testing Runs
Model fitting
Training Inputs
Testing Inputs
Prediction of testing runs by the metamodel
Notes: Basic workflow of constructing a metamodel
We run TRACE to train the metamodel
Independently to that we also run TRACE to create testing data
We we test the metamodel performance we compare its prediction against the output real TRACE run

## Slide 18: Dealing with Multivariate Output: Principal Component Analysis
Output of the TRACE model of FEBA is highly multivariate.
Output Type | # of outputs
Clad Temperature | 
Pressure Drop | 
Liquid Carryover | 
Output Type | 
Clad Temperature | 
Pressure Drop | 
Liquid Carryover | 
Dimension reduction by Principal Component Analysis (PCA)
SVD
Concatenate and centered outputs
Eigenvectors (principal components)
PC scores
PC scores, predicted by GP metamodel
the mean of output
Mean and 1st PC of clad temperature output
Prediction of multivariate output
Notes: W is a scalar associated with a particular realization
V is eigenvector shared with all realizations
There are many eigenvectors but they are stacked with decreasing variance contribution
Note that Q is the number of retained principal components used to reconstruct the full output space and it is in this examples is typicaly less than 10.
And we simply need to construct metamodels predicting the scores of that selected PC.
The number was selected based on compromise between gained improvement and the difficulty to fit a GP metamodel.

## Slide 19: Principal Component Analysis (PCA): Liquid Carryover Output
Notes: Here’s what I mean

## Slide 20: PC – GP Metamodel: Liquid Carryover Output
Notes: Here’s what I mean

## Slide 21: Principal Component Analysis (PCA): Clad Temperature Output
Dimension reduction by Principal Component Analysis (PCA)
SVD
Concatenate and centered outputs
Eigenvectors (principal components)
PC scores
PC scores, predicted by GP metamodel
the mean of output
Mean and 1st PC of clad temperature output
Prediction of multivariate output
Notes: Here’s what I mean

## Slide 22: PC – GP Metamodel: Clad Temperature Output
Dimension reduction by Principal Component Analysis (PCA)
SVD
Concatenate and centered outputs
Eigenvectors (principal components)
PC scores
PC scores, predicted by GP metamodel
the mean of output
Mean and 1st PC of clad temperature output
Prediction of multivariate output
Notes: Here’s what I mean

## Slide 23: Constructing GP Metamodel: Training and Testing
Testing
Design of Experiment
Training Runs
Testing Runs
Model fitting
Different factors involved in the construction of GP Metamodel
Training Inputs
Testing Inputs
Notes: We find out that the size of training sample is the main factor determining the predictive performance of the metamodel

## Slide 24: Testing the Metamodel against Testing Samples
Metamodel predictive performance is assessed by comparison against large independent test data (i.e. actual TRACE runs)
Dimension reduction error
Due to smaller to reconstruct the full output space
X-axis:
Y-axis:
Dimension reduction error and GP error
Due to (also) miss-prediction of PC scores
Both are in terms of RMSE
Notes: If the points are in line then the GP predicts perfectly the
If above the line then the GP metamodel mispredict
From left to right the error is due to Dimension reduction error

## Slide 25: Testing the Metamodel against Testing Samples ()
Clad Temperature [K]
Pressure Drop [Pa]
Liquid Carryover [kg]
GP PC RMSE
Testing Samples
Metamodel predictive performanceis acceptable for each output
Notes: The metamodel prediction is limited by the error due to dimension reduction
It also shows that we cannot go better than the error given by the metamodel.
In context it is find for the time being as the prior uncertainty gives a larger error (standard deviation)

## Slide 26: Statistical Framework (3/4): Bayesian Calibration
1. Global Sensitivity Analysis
2. Metamodeling
3. Bayesian Calibration
How to select the important parameters?
How to approximate the input/output of a computer model?
How to make the uncertainty quantification?
27 initial parameters
12 influential parameters
Wide, independent prior uncertainties
Use experimental data to constrain the prior

## Slide 27: Bayesian Calibration, Inverse Quantification: Uncertain (Inputs + Data) Uncertain Inputs Updated
Bayes’ Theorem
Forward Model
Uncertain model parameters (posterior)
Likelihood
Experimental Data from SETF
Additional sources of uncertainty
Uncertain model parameters (prior)
Controllable inputs (w.r.t experiment)
Probability of observing data given parameters

## Slide 28: Normal Likelihood
GP metamodel
Principal Comp. truncation
Model bias
measurement
Multiple sources of variance
Likelihood
Model prediction
Model bias
Measurement error
Experimental Data
6 calibration schemes were investigated:
Considering different types of data
With or without model bias term
Excluding a model parameter
GP
GP
Gaussian
given
unknown
Notes: We will go through the main results provided by the first 4 schems
Note that no xc means we only deal with the calibration of the 8 model parameters.

## Slide 29: Posterior Formulation and Computation
Bayes’ Theorem
Posterior
Likelihood
Prior
Uncertainty on is fully specified by , the posterior pdf.
Markov Chain Monte Carlo (MCMC) Simulation
How is used:
  Uncertainty propagation in an application setting (integration of a function under the posterior pdf)
  Characterization of parameter uncertainty, e.g., moments (integration of the pdf over the parameter space)
Notes: Note that posterior is a multidimensional probability density function
MH in a nutshell
We actually use Ensemble MCMC
samples generated
Converge after of the way
How are we using p(xm) either to characterize xm (by its moments for instance) or used to integrate in the propagation fashion or
MH in a nutshell
We actually use Ensemble MCMC
2×10^6 samples generated
Converge after 2/5 of the way
How are we using p(xm) either to characterize xm (by its moments for instance) or used to integrate in the propagation fashion or

## Slide 31: Prior uncertainty of the model parameters
gridHT
iafbWHT
dffbWHT
dffbVIHT
iafbIntDr
dffbIntDr
dffbWDr
tQuench
Diagonal panels: univariate marginal PDFs
Off-diagonal panels: pairwise correlation plots (bright color = concentrated samples)
Notes: Can the data and the calibration model can be used to constrain this prior?
Start by explaining how to read the figure: diagonal panels (univariate marginals pdf)
The vertical lines in the diagonal is the 95% credible interval
Off-diagonal panels: bivariate marginals
Explain column and row
Say that these are the 8 model parameters we are left with to be calibrated, I will mention it if necessary

## Slide 32: The posterior uncertainty based on pressure drop data only (samples)
gridHT
iafbWHT
dffbWHT
dffbVIHT
iafbIntDr
dffbIntDr
dffbWDr
tQuench
Interfacial drag of the inverted annular flow regime
Notes: Pressure drop data manage to constrain some of the parameter mainly iafbIntDr

## Slide 33: Posterior on all types of data (samples)
gridHT
iafbWHT
dffbWHT
dffbVIHT
iafbIntDr
dffbIntDr
dffbWDr
tQuench
Vapor-Interface HTC of the DFFB
Spacer grid HTC enhancement
Interfacial drag of the DFFB
Wall HTC of the DFFB
Notes: Data can help constrain the prior range of the model parameters. (only small part of the prior that is consistent with the calibration data)
The white, the white, the white (example gridHT)
But the posterior samples also exhibit correlation among the parameters. You can see this from the structure that can be observed in the posterior samples.
Illustrate why it makes sense that dffbVIHT and dffbIntDr are correlated from the physical point of view

## Slide 34: Posterior on all types of data (samples)
gridHT
iafbWHT
dffbWHT
dffbVIHT
iafbIntDr
dffbIntDr
dffbWDr
tQuench
Vapor-Interface HTC of the DFFB
Interfacial drag of the DFFB
Notes: Data can help constrain the prior range of the model parameters. (only small part of the prior that is consistent with the calibration data)
The white, the white, the white (example gridHT)
But the posterior samples also exhibit correlation among the parameters. You can see this from the structure that can be observed in the posterior samples.
Illustrate why it makes sense that dffbVIHT and dffbIntDr are correlated from the physical point of view

## Slide 35: Posterior Samples are Correlated (i.e., a set of “collectively-fitted” values)
Time [s]
Clad Temperature [K]
Middle assembly
Top assembly
Uncertainty propagation on FEBA Test. No. 216 (the calibration data) based on 1’000 Monte Carlo samples.
Prior
Posterior, Correlated
Posterior, Independent
Exp. Data
Notes: A set of “collectively-fitted” values which means that if we don’t consider them as a collection then the prediction would less match the calibration data itself.
If we only consider the univariate marginals (neglecting correlation) we obtain prediction that is less consistent with the calibration data.
Only if we consider the posterior samples jointly, that the prediction match the experimental data better.

## Slide 36: Statistical Framework (4/4): Posterior Uncertainty Propagation
1. Global Sensitivity Analysis
2. Metamodeling
3. Bayesian Calibration
How to select important parameters to be inferred?
How to approximate the input/output of a computer model?
How to make the uncertainty quantification?
How good is the quantified uncertainty?
27 initial parameters
12 influential parameters
Wide, independent prior uncertainties
Narrower, correlated posterior uncertainties
4. Uncertainty Propagation
Wide prior prediction uncertainties
Propagate posterior uncertainties for different experimental conditions

## Slide 37: Comparing Different Calibration Results: Informativeness
Two scores to summarize and compare results of uncertainty propagation using different posterior samples w.r.t the prior
LUB: Lower Uncertainty Bound
( prediction percentile)
( prediction percentile)
UUB: Upper Uncertainty Bound
Informativeness for output
Posterior prediction uncertainty is equal to that of the prior
No posterior prediction uncertainty
Notes: Think of a posterior prediction is a source of information for output y and defined only in three values, the lower uncertainty bound, the upper uncertainty bound and the reference value
Informativeness tries to measure the width of posterior uncertainty band relative to that of the prior
Main message: large informativeness means narrower band

## Slide 38: Comparing Different Calibration Results: Calibration Score
Two scores to summarize and compare results of uncertainty propagation using different posterior samples w.r.t the prior
Calibration Score for output
Experimental data falls outside the uncertainty band
Experimental data matches the reference value exactly
The height of the experimental data in the information triangle
: Reference value
( prediction percentile; median)
Notes: Calibration measure the location of experimental data inside the so called “information” triangle
large calibration means closer to experimental data, while lower often means the band covers less experimental data

## Slide 39: Posterior Prediction Uncertainty in Terms of Calibration Score and Informativeness
Informativeness [-]
Calibration Scheme
All Parameters, Correlated
All Parameters, Independent
Calibration Score [-]
Prior
Posterior, Correlated
Posterior, Independent
Exp. Data
Notes: Begin by explaining how to read the figure
Vertical line
Horizontal line (Less “calibrated” here means cover less experimental data points)
The location of the points
The effect of not considering correlation
Because calibration score is highly penalizing. But the point of the measure is to check whether there is pattern across experimental conditions.

## Slide 40: Effects of Experimental Conditions on Posterior Prediction Uncertainty
Calibration Scheme
All Parameters, Correlated
All Parameters, Independent
Informativeness [-]
Calibration Score [-]
Informativeness [-]
Calibration Score [-]
Notes: There is no strong pattern of discrepancy
Yes the calibration score falls for all, but it is because fail to cover the experimental data by the band is highly penalizing. What we are interested in this comparison, especially to indicate whether the overfitting occurs severely is to look at the different prior and posterior calibration and compare with the results of Test 216. If the difference is larger than it would slightly overfit. There is no significant overfitting based on this difference.

## Slide 41: Removing a Highly Correlated Influential Parameter from the Calibration
Calibration Scheme
All Parameters, Independent
All Parameters, Correlated
Excl. dffbVIHT, Independent
Excl. dffbVIHT, Correlated
Calibration Score [-]
Informativeness [-]
dffbVIHT
dffbIntDr
Vapor-Interface HTC of the DFFB
Interfacial drag of the DFFB
Notes: Yet there is reason to be prudent when it comes to correlation. (univariate marginal) Parameter uncertainty can be wide (indicating no overfitting) but the correlation can cause such overfitting nevertheless.
Why the triangle is now there? Investigation on the influential and strongly correlated parameter
The location of the triangle in the graph
Mention that now the difference between the two triangle is really minor meaning the correlation becomes less influential

## Slide 42: Effects of Experimental Conditions on Posterior Prediction Uncertainty
Calibration Scheme
All Parameters, Independent
All Parameters, Correlated
Excl. dffbVIHT, Independent
Excl. dffbVIHT, Correlated
Calibration Score [-]
Calibration Score [-]
Informativeness [-]
Informativeness [-]
Notes: The same pattern across different experimental condition

## Slide 43: Conclusion
Consolidation, implementation, and application of tools based on statistical framework for quantifying the physical model parameters in the TRACE code
Motivation:
Objectives:
Contribution:
Given data from a separate effect test facility, develop a methodology to systematically quantify the uncertainty of the parameters in the TRACE code
Uncertainty in physical model parameters are often derived mainly based on expert-judgment and on a particular experimental data

## Slide 44: Contributions: Demonstration of the Methodology on the FEBA TRACE Model
1. Global Sensitivity Analysis
2. Metamodeling
3. Bayesian Calibration
How to select important model parameters?
How to approximate the input/output of a computer model?
How to make the quantification?
27 initial parameters
12 influential parameters
Wide, independent prior uncertainties
Narrower, correlated posterior uncertainties
4. Uncertainty Propagation
Narrower posterior prediction uncertainties for all exp. conditions
Wide prior prediction uncertainties
How good is the quantified uncertainty?
Notes: And through the thesis itself it is demonstrated that
FEBA TRACE model is a relatively small and simple model, but it is by no means a toy model. It illustrates a typical analysis of calibrating TRACE model parameters based on SETF

## Slide 45: Contributions
Developed Tools:
trace-simexp Python3 command line utilities for conducting simulation experiment of a TRACE model of Separate effect test facility
gsa-module Python3 module implementing various design of experiments and global sensitivity analysis methods (e.g. Morris and Sobol’ indices est.)
Publications and other contributions:
4 International conference papers
1 journal article
2 submissions to the OECD/NEA PREMIUM benchmark Phase 4
2 contributions to the OECD/NEA PREMIUM reports
1 PSI technical report
Notes: Two additional publications outside the scope the thesis are co-authored using the developed tools

## Slide 46: Upcoming Challenges
Bayesian Calibration
Uncertainty Propagation
  216
  214
How to summarize generic correlation structure of the posterior useful for downstream analysis?
Calibration was only done based on one dataset. Error structure might differ
Sequential calibration against other SETF remains open question
ACHILLES
RBHT
  220
  222
  223
  218
FEBA
Notes: We calibrate only with one (and we did verify against different test data), but its performance depends on the assume error structure that derived only with the aforementioned calibration data. We need to simultaneously consider
We don’t often consider correlation among model parameters, but calibration will result in a correlated posterior. Consistent propagation requires this information to be carried.
What is the repercussion in practice when we have to consider such correlation in the model parameters.

## Slide 47: Wir schaffen Wissen – heute für morgen
Thank you for your attention.
My sincere gratitude to:
Prof. A. Pautz
Mr. O. Zerkak
Dr. G. Perret
Mr. Ph. Jacquemoud
Dr. M. Hursin
Dr. D. Rochman
Dr. I. Clifford
Mr. H. Ferroukhi
Other members of STARS
The jury members:
Dr. J. Baccou
Prof. R. Houdré
Prof. B. Sudret
Dr. W. Zwermann
Additional acknowledgments:
Swiss Federal Nuclear Safety Inspectorate (ENSI)
Swiss Federal Office of Energy (BFE)
“Global Sensitivity Analysis of Transient Code Output applied to a Reflood Experiment Model using TRACE Code,” NSE, vol. 184, no. 6, 2016.
“Bayesian Calibration of Thermal-Hydraulics Model with Time-Dependent Output,” NUTHOS-11, 2016.
“A Methodology for Global Sensitivity Analysis of Transient Code Output applied to Reflood Experiment Model using TRACE,” NURETH-16, 2015.
“Sensitivity Analysis of Bottom Reflood Simulation using the Morris Screening Method,” NUTHOS-10, 2014.
“Exploring Variability in Reflood Simulation Results: an Application of Functional Data Analysis,” NUTHOS-10, 2014.

## Slide 48: Dealing with Multivariate Output: Principal Component Analysis
Output of the TRACE model of FEBA is highly multivariate.
Output Type | # of outputs
Clad Temperature | 
Pressure Drop | 
Liquid Carryover | 
Output Type | 
Clad Temperature | 
Pressure Drop | 
Liquid Carryover | 
Dimension reduction by Principal Component Analysis (PCA)
SVD
Concatenate and centered outputs
Eigenvectors (principal components)
PC scores
PC scores, predicted by GP metamodel
the mean of output
Mean and 1st PC of clad temperature output
Prediction of multivariate output
Notes: W is a scalar associated with a particular realization
V is eigenvector shared with all realizations
There are many eigenvectors but they are stacked with decreasing variance contribution
Note that Q is the number of retained principal components used to reconstruct the full output space and it is in this examples is typicaly less than 10.
And we simply need to construct metamodels predicting the scores of that selected PC.
The number was selected based on compromise between gained improvement and the difficulty to fit a GP metamodel.